## 27MAR-02APR17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | SAMAGURI | AS-18 | SAMAGURI-MISA -2 | NP-5796-A | N | Y | N | 2016-03-28 | MISA-2 END DATA USED | REPLACE METER |  | Time Drift>8 Minutes
2 | ASSAM | SAMAGURI | AS-17 | SAMAGURI-MISA -1 | NP-5797-A | N | Y | N | 2016-03-28 | MISA-1 END DATA USED | REPLACE METER |  | Time Drift>8 Minutes
3 | ASSAM | TINSUKIA | AS-74 | TINSUKIA-KATHALGURI | NP-8386-A | N | N | Y | 2016-03-27 | KATHALGURI END DATA USED |  | 06/04/2016 | 1/2 READING
4 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
5 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
6 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR

## 3APR-09APR17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | SAMAGURI | AS-18 | SAMAGURI-MISA -2 | NP-5796-A | N | Y | N | 2016-03-28 | MISA-2 END DATA USED | REPLACE METER |  | Time Drift>8 Minutes
2 | ASSAM | SAMAGURI | AS-17 | SAMAGURI-MISA -1 | NP-5797-A | N | Y | N | 2016-03-28 | MISA-1 END DATA USED | REPLACE METER |  | Time Drift>8 Minutes
3 | ASSAM | TINSUKIA | AS-74 | TINSUKIA-KATHALGURI | NP-8386-A | N | N | Y | 2016-03-27 | KATHALGURI END DATA USED |  | 06/04/2016 | 1/2 READING
4 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
5 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
6 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR

## 10APR-16APR17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | SAMAGURI | AS-18 | SAMAGURI-MISA -2 | NP-5796-A | N | Y | N | 2016-03-28 | MISA-2 END DATA USED | REPLACE METER |  | Time Drift>8 Minutes
2 | ASSAM | SAMAGURI | AS-17 | SAMAGURI-MISA -1 | NP-5797-A | N | Y | N | 2016-03-28 | MISA-1 END DATA USED | REPLACE METER |  | Time Drift>8 Minutes
3 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
4 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
5 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR

## 17APR-23APR17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | SAMAGURI | AS-18 | SAMAGURI-MISA -2 | NP-5796-A | N | Y | N | 2016-03-28 | MISA-2 END DATA USED | REPLACE METER |  | Time Drift>8 Minutes
2 | ASSAM | SAMAGURI | AS-17 | SAMAGURI-MISA -1 | NP-5797-A | N | Y | N | 2016-03-28 | MISA-1 END DATA USED | REPLACE METER |  | Time Drift>8 Minutes
3 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
4 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
5 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR

## 24APR-30APR17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
2 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
3 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR

## 01MAY-07MAY17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
2 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
3 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR

## 08MAY-14MAY17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
2 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
3 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
4 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
5 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
6 | ASSAM | AGIA | AS-86 | AGIA END OF NANGALBIBRA | NP-8484-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
7 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
8 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes

## 15MAY-21MAY17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
2 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
3 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
4 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
5 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
6 | ASSAM | AGIA | AS-86 | AGIA END OF NANGALBIBRA | NP-8484-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
7 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
8 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes

## 22MAY-28MAY 17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
2 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
3 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
4 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
5 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
6 | ASSAM | AGIA | AS-86 | AGIA END OF NANGALBIBRA | NP-8484-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
7 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
8 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes

## 29MAY-04JUNE 17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
2 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
3 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
4 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
5 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
6 | ASSAM | AGIA | AS-86 | AGIA END OF NANGALBIBRA | NP-8484-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
7 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
8 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes

## 05JUN-11JUNE 17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
2 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
3 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
4 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
5 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
6 | ASSAM | AGIA | AS-86 | AGIA END OF NANGALBIBRA | NP-8484-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
7 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
8 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes

## 12JUN-18JUNE 17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
2 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
3 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
4 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
5 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
6 | ASSAM | AGIA | AS-86 | AGIA END OF NANGALBIBRA | NP-8484-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
7 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
8 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes

## 19JUN-25JUNE 17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | PANCHGRAM | AS-79 | PANCHGRAM-SILCHAR | NP-7594-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
2 | ASSAM | PANCHGRAM | AS-06 | PANCHGRAM-LUMSNONG | NP-6876-A | N | Y | N | 2016-04-01 | SILCHAR END DATA USED | REPLACE METER |  | Time Drift>5 Minutes
3 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
4 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
5 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
6 | ASSAM | AGIA | AS-86 | AGIA END OF NANGALBIBRA | NP-8484-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
7 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes
8 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTION |  | Time Drift>5 Minutes

## 26JUN-02JUL17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
2 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | ASSAM | AGIA | AS-86 | AGIA END OF NANGALBIBRA | NP-8484-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
5 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
6 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes

## 03JUL-09JUL17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
2 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END IS USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
5 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
6 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
7 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END IS READING 1/3 OF RANGANADI END

## 10JUL-16JUL17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
2 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END IS USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
5 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
6 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
7 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END IS READING 1/3 OF RANGANADI END

## 17JUL-23JUL17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | TRIPURA | SJM'NAGAR | TR-13 | SJMNGR-PTANA | NP-8471-A | Y | N | N | 2016-04-01 | PALATANA END DATA USED | CHECK CT |  | READING ERROR IN SJMNGR
2 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END IS USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
5 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
6 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
7 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END IS READING 1/3 OF RANGANADI END
8 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
9 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT

## 24JUL-30JUL17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END IS USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
5 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
6 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END IS READING 1/3 OF RANGANADI END
7 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
8 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
9 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR(PG) END OF BOKAJAN FDR | NP-5287-A | N | Y | N | 2017-07-17 | BOKAJAN END USED | DRIFT CORRECTIION |  | Time Drift>30 Minutes

## 31JUL-06AUG17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END IS USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
5 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
6 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END IS READING 1/3 OF RANGANADI END
7 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
8 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
9 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR(PG) END OF BOKAJAN FDR | NP-5287-A | N | Y | N | 2017-07-17 | BOKAJAN END USED | DRIFT CORRECTIION |  | Time Drift>30 Minutes

## 07Aug-13AUG17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END IS USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | DIMAPUR | NG-01 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8385-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION | 2017-08-10 | Time Drift>5 Minutes
5 | POWERGRID | DIMAPUR | NG-17 | DIMAPUR(PG) END OF DIMAPUR(S) I FDR | NP-8481-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION | 2017-08-10 | Time Drift>5 Minutes
6 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END IS READING 1/3 OF RANGANADI END
7 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
8 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
9 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR(PG) END OF BOKAJAN FDR | NP-5287-A | N | Y | N | 2017-07-17 | BOKAJAN END USED | DRIFT CORRECTIION | 2017-08-10 | Time Drift>30 Minutes

## 14Aug-20AUG17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END IS USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END IS READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT

## 21Aug-27AUG17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END IS USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END IS READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT

## 28Aug-03SEP17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END IS USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END IS READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT

## 04SEP-10SEP17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
7 | KOPILI | KOPILI | KK-21 | KOPILI END OF KHANDONG II | NP-8610-A | Y | N | N | 2017-09-04 | KHANDONG END USED | CHECK CT | 2017-09-10
8 | ASSAM | MOTONGA | ER-08 | MOTONGA END OF RANGIA | NP-8380-A | Y | N | N | 08/0917 | NIL | CHECK CT |  | MOTANGA END READING 40% LOWER COMPARED TO RANGIA END,ISSUE RESOLVED

## 11SEP-17SEP17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
7 | ASSAM | MOTONGA | ER-08 | MOTONGA END OF RANGIA | NP-8380-A | Y | N | N | 08/0917 | NIL | CHECK CT | 2017-09-14 | MOTANGA END READING 40% LOWER COMPARED TO RANGIA END

## 18SEP-24SEP17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT

## 25SEP-01OCT17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT

## 02OCT-08OCT17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
7 | POWERGRID | SILCHAR | AS-84 | SILCHAR END OF PALATANA-II | NP-8660-A | Y | N | N | 2017-10-02 | PALATANA END USED | CHECK CT

## 09OCT-15OCT17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
7 | POWERGRID | SILCHAR | AS-84 | SILCHAR END OF PALATANA-II | NP-8660-A | Y | N | N | 2017-10-02 | PALATANA END USED | CHECK CT | 2017-10-10 | ISSUE RESOLVED

## 16OCT-22OCT17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT

## 23OCT-29OCT17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT

## 30OCT-05NOV17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT

## 06NOV-12NOV17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
8 | POWERGRID | SALAKATI | AS-30 | SALAKATI END OF BTPS 1 | NP-9434-A | Y | N | N | 2017-11-06 | OTHER END USED | CHECK CT |  | SALAKATI END READING 1/3 of BTPS END
9 | POWERGRID | AIZAWL | MZ-08 | AIZAWL END OF KOLASIB | NP-8486-A | Y | N | N | 2017-11-06 |  | CHECK CT |  | AIZAWL END READING 2/3 OF KOLASIB END

## 13NOV-19NOV17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
8 | POWERGRID | SALAKATI | AS-30 | SALAKATI END OF BTPS 1 | NP-9434-A | Y | N | N | 2017-11-06 | OTHER END USED | CHECK CT |  | SALAKATI END READING 1/3 of BTPS END
9 | POWERGRID | AIZAWL | MZ-08 | AIZAWL END OF KOLASIB | NP-8486-A | Y | N | N | 2017-11-06 |  | CHECK CT |  | AIZAWL END READING 2/3 OF KOLASIB END
10 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END

## 20NOV-26NOV17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
8 | POWERGRID | SALAKATI | AS-30 | SALAKATI END OF BTPS 1 | NP-9434-A | Y | N | N | 2017-11-06 | OTHER END USED | CHECK CT | 2017-11-21 | SALAKATI END READING 1/3 of BTPS END
9 | POWERGRID | AIZAWL | MZ-08 | AIZAWL END OF KOLASIB | NP-8486-A | Y | N | N | 2017-11-06 |  | CHECK CT | 2017-11-21 | AIZAWL END READING 2/3 OF KOLASIB END
10 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
11 | POWERGRID | Bongaigaon(PG) | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | N | Y | 2017-11-20 | OTHER END USED

## 27NOV-03DEC17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
7 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
8 | POWERGRID | Bongaigaon(PG) | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | N | Y | 2017-11-20 | OTHER END USED

## 04DEC-10DEC17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION |  | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION |  | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
7 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
8 | POWERGRID | Bongaigaon(PG) | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | N | Y | 2017-11-20 | OTHER END USED

## 11DEC-17DEC17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | ASSAM | AZARA | AS-93 | AZARA END OF 400 KV SILCHAR | NP-8588-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION | 2017-12-17 | Time Drift>5 Minutes
2 | ASSAM | AZARA | AM-01 | AZARA END OF 400 KV BONGAIGAON | NP-8658-A | N | Y | N | 2017-05-15 | NIL | DRIFT CORRECTIION | 2017-12-17 | Time Drift>5 Minutes
3 | ASSAM | AGIA | AS-86 | AGIA END OF mendipathar | NP-8484-A | N | Y | N | 2017-05-15 | MENDIPATHAR END USED | DRIFT CORRECTIION | 2017-12-17 | Time Drift>5 Minutes
4 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
5 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
6 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
7 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
8 | POWERGRID | Bongaigaon(PG) | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | N | Y | 2017-11-20 | OTHER END USED
9 | POWERGRID | MOTONGA | ER-08 | Motonga end of 132 kV Rangia | NP-8380-A | N | N | Y | 2017-12-11 | OTHER END USED |  | 2017-12-17 | Meter is not communicating with DCD

## 18DEC-24DEC17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | Bongaigaon(PG) | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | N | Y | 2017-11-20 | OTHER END USED |  |  | One CVT fuse blown
2 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
3 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
5 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END

## 25DEC-31DEC17
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | Bongaigaon(PG) | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | N | Y | 2017-11-20 | OTHER END USED |  |  | One CVT fuse blown
2 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
3 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
5 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END

## 01JAN-07JAN18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | Bongaigaon(PG) | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | N | Y | 2017-11-20 | OTHER END USED |  |  | One CVT fuse blown
2 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
3 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
5 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END

## 08JAN-14JAN18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | Bongaigaon(PG) | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | N | Y | 2017-11-20 | OTHER END USED |  |  | One CVT fuse blown
2 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
3 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
5 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END

## 15JAN-21JAN18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | Bongaigaon(PG) | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | N | Y | 2017-11-20 | OTHER END USED |  |  | One CVT fuse blown
2 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
3 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
5 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END

## 22JAN-28JAN18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
3 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END

## 29JAN-04FEB18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
3 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END

## 05FEB-11FEB18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
3 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END

## 12FEB-18FEB18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
3 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
5 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE

## 19FEB-25FEB18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
3 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
5 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE

## 26FEB-04MAR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
3 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT
4 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
5 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE

## 05-11MAR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | MANIPUR | IMPHAL | MN-01 | IMPH(S) END OF IMPH(PG) | NP-6950-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT | 2018-03-11
3 | MANIPUR | IMPHAL | ZZ-01 | IMPH(S) END OF IMPH(PG)II | NP-8374-A | Y | N | N | 2017-07-17 | POWERGRID END USED | CHECK CT | 2018-03-11
4 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
5 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE

## 12-18MAR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE

## 19-25MAR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE

## 26 MAR-01APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE

## 02 APR-08APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED

## 09 APR-15APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED

## 16APR-22APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16

## 23APR-29APR18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16

## 30APR-06MAY18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
10 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED

## 07MAY-13MAY18
Interconnection metering error
Sl. No. | utility Name | Location/Sub Station | Location code | Name of Feeder | Meter Serial Number | Error in Meter related to (CT/PT) (Y or N) | Error in Meter due to Time drift (Y or N) | Error in Meter due to any other reason (Y or N) | Date of start of problem | Description of Alternate Arrangement done for computation | Action required by utilities | Date of problem attended/removal (Date) | Remarks
|  | A | B | C | D | E | F | G | H | I | J | K | L
1 | POWERGRID | BALIPARA | AS-45 | BALIPARA END OF RANGANADI FDR-2 | NP-5308-A | Y | N | N | 2017-07-03 | NIL | CHECK CT |  | BALIPARA END READING 1/3 OF RANGANADI END
2 | ASSAM | DULLAVCHERRA | AS-08 | DULLAVCHERRA END OF D'NGAR FDR | NP-6946-A | N | N | Y | 2017-11-13 | OTHER END USED |  |  | DULLAVCHERRA END IS READING 10% OF THE OTHER END
3 | POWERGRID | JIRIBAM | MN-12 | JIRIBAM(PG) END OF JIRIBAM(MAN) FDR | NP-8500-A | N | N | Y | 2018-02-12 | OTHER END USED |  |  | JIRIBAM(PG) END IS READING ZERO VALUE
4 | POWERGRID | DIMAPUR | NG-08 | DIMAPUR END OF 132KV BOKAJAN FDR | NP-9451-A | Y | N | N | 2018-04-02 | OTHER END USED
5 | POWERGRID | BONGAIGAON | AS-96 | Bongaigaon(PG) END OF 400 KV ALIPURDUAR 1 | NP-9072-A | N | Y | N | 2018-04-16
6 | POWERGRID | BONGAIGAON | AS-25 | BONG END OF BINAGURI-1 FEEDER | NP-8468-A | N | Y | N | 2018-04-16
7 | POWERGRID | BONGAIGAON | AS-26 | BONG END OF BINAGURI-2 FEEDER | NP-8469-A | N | Y | N | 2018-04-16
8 | NTPC | NTPC | NT-11 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-1 LNT METER | NP-5812-A | N | Y | N | 2018-04-16
9 | NTPC | NTPC | NT-12 | NTPC END OF 400 KV NTPC(B'GAON)-B'GAON(PG)-2 LNT METER | NP-5793-A | N | Y | N | 2018-04-16
10 | MANIPUR | IMPHAL(S) | ZZ-01 NP-8374-A | Imphal(S) END OF IMP(PG)-II FDR | NP-8374-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
11 | MANIPUR | IMPHAL(S) | MN-01 | IMPHAL(S) END OF IMPH PG FDR-I | NP-6950-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
12 | TRIPURA | 79 TILLA | TR-01 | AGARTALA END OF AGTPP-1 FDR | NP-6850-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED
13 | TRIPURA | 79 TILLA | TR-02 | AGARTALA END OF AGTPP-2 FDR | NP-6851-A | N | Y | N | 2018-04-30 |  |  |  | OTHER END USED