## 31 MAR 25-06 APR 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | POWERGRID | IMPHAL | ZZ-72 | 132/33 kV IMPHAL ICT- 2 LV SIDE | NP-9963-A | Erroneous reading (close to 33%) | 14.08.2023 | 15:30 Hrs of 27-03-2025 | IMPHAL | LV side CT replaced as per information from Site.
2 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
3 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
4 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
5 | MANIPUR | NINGTHOUKHONG | MN-32 | 132 KV NINGTHOUKHONG - IMPHAL(PG) 2 | NE-0151-A | Erroneous reading. Sign Reversal | 13:45 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT reversal to be checked
6 | MANIPUR | NINGTHOUKHONG | MN-33 | 133 KV NINGTHOUKHONG - IMPHAL(PG) 3 | NE-0152-A | Erroneous reading. Reads 33% | 14:15 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting or two phase reversal to be checked
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | MANIPUR | NINGTHOUKHONG | MN-33 | Ningthoukhong-PGCI-3 | NE-0152-A | High time drift | 2025-03-31 | Till end of the week | NINGTHOUKHONG | Other end meter used for drawal computation; time drift corrective action required
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | NEEPCO | KHANDONG |  | Khnd. Stage_II | NE-0091-A | Check Meter | Weekly Drift correction required
3 | NEEPCO | KHANDONG |  | 3 Mva X’er | NE-0172-A | Check Meter | Weekly Drift correction required
4 | NEEPCO | KHANDONG |  | Umrongso Fdr | NE-0136-A | Main Meter | Weekly Drift correction required
5 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
6 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
9 | ASSAM | MIRZA |  | Bongaigaon 400 kV | NP-9983-A | Main Meter | Weekly Drift correction required
11 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
8 | STERLITE | HATSINGIMARI |  | 132 kV Ampati - Hatsingimari CKT-2 (Bay-107) | NE-0096-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
| MANIPUR | NINGTHOUKHONG |  | Loktak Incomer | NP-9651-A | Standby Meter | Weekly Drift correction required
| MANIPUR | NINGTHOUKHONG |  | Ningthoukhong-PGCI-2 | NE-0151-A | Standby Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Check Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
10 | POWERGRID/ASSAM | SILCHAR |  | 400kV ICT 1 | NE-0050-A | Standby Meter | Weekly Drift correction required
10 | POWERGRID/ASSAM | MISA |  | Samaguri # 1 | NP 9501 A | Main Meter | Weekly Drift correction required
10 | POWERGRID/ASSAM | MISA |  | ICT#1 400 KV SIDE | NP 5300 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID/ASSAM | MISA |  | Silchar #2 | NP 9929 A | Standby Meter | Weekly Drift correction required
10 | POWERGRID/ASSAM | MISA |  | 220 kV KOPILI #3 | NE 0063 A | Standby Meter | Weekly Drift correction required
7 | POWERGRID | HAFLONG |  | BAY NO 102 HAFLONG-UMRANGSHO | NP-8502-A | Standby Meter | Weekly Drift correction required
7 | POWERGRID | HAFLONG |  | HAFLONG AEGCL END | NE-0026-A | Main Meter | Weekly Drift correction required
16 | POWERGRID | NIRJULI |  | ICT-II HV | NP-9662 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | KOHIMA | NP-8472-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BNC |  | LOWER SUBANSIRI-CKT-2 | NE-0150-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 220/132 KV ICT-1(HV) | NP-6868-A | Standby Meter | Weekly Drift correction required
22 | NEEPCO | PARE |  | 132KV PARE- UNIT I | NP 9554 A | Standby Meter | Weekly Drift correction required
23 | NEEPCO | PARE |  | 132KV PARE-RANGANADI 2 | NP 9538 A | Main Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | TRIPURA | DHARMANAGAR | Time drift report not received
4 | MIZORAM | LUANGMUAL | Time drift report not received
5 | MANIPUR | TIPAIMUKH | Time drift report not received
6 | TRIPURA | AMBASSA | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NEEPCO | DOYANG | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | ARUNACHAL PRADESH | TENGA | Time drift report not received
11 | POWERGRID | SALAKATI | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
3 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
4 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
5 | NAGALAND | SANIS | Not Received. Mailed to concerened
6 | POWERGRID | NINGTHOUKHONG | Mail Received on 09-04-2025

## 07 APR 25-13 APR 2025
1. मीटर रीडिंग विसंगति/ Meter Reading Discripency
A. मीटरों में सीटी/पीटी त्रुटि होने का संदेह है/ Meters suspected to have CT/PT error
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | BUDHJUNGNAGAR | TR-27 | 132 kV BUDHJUNGNAGAR (TSECL) END OF SM NAGAR (INDIGRID) FDR | NP-9943-A | Sign Reversal | 2023-12-04 | Till end of the week | BUDHJUNGNAGAR | Other end meter used for drawal computation; CT connectivity checking required
2 | INDIGRID | SM NAGAR | ZZ-47 | 400 kV SM NAGAR (INDIGRID) END OF 400 kV PK BARI (INDIGRID) I | NP-9978-A | Reads 66 % less | 2024-02-12 | Till end of the week | SM NAGAR | CT connectivity checking required
3 | TRIPURA | DHARMANAGAR | TR-06 | 132 kV DHARMANAGAR END OF DULLAVCHERA FDR | NP-6892-B | Erratic Reading (Around 75%). | 00:00 Hrs of 30-06-2024 | Till end of the week | DHARMANAGAR | Other end meter used for injection computation; CT/CVT connectivity checking required
4 | MANIPUR | NINGTHOUKHONG | MN-32 | 132 KV NINGTHOUKHONG - IMPHAL(PG) 2 | NE-0151-A | Erroneous reading. Sign Reversal | 13:45 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT reversal to be checked
5 | MANIPUR | NINGTHOUKHONG | MN-33 | 133 KV NINGTHOUKHONG - IMPHAL(PG) 3 | NE-0152-A | Erroneous reading. Reads 33% | 14:15 Hrs of 21-02-2025 | Till end of the week | NINGTHOUKHONG | CT/CVT connectivity checking required. CT shorting or two phase reversal to be checked
B. किसी अन्य कारण से मीटर में गड़बड़ी/ Meter error due to any other reason
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | स्थान संहिता / Location Code | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | मीटर में त्रुटि /Error in Meter | आरंभ अवधि / Duration from | अवधि तक / Duration to | सुधारात्मक कार्रवाई अपेक्षित / Corrective Action required from | टिप्पणी / Remarks
1 | TRIPURA | UDAIPUR | TR-14 | 132 kV UDAIPUR END OF PALATANA | NP-8470-A | High time drift | 2023-10-16 | Till end of the week | UDAIPUR | Other end meter used for drawal computation; time drift corrective action required
2 | MANIPUR | NINGTHOUKHONG | MN-33 | Ningthoukhong-PGCI-3 | NE-0152-A | High time drift | 2025-03-31 | Till end of the week | NINGTHOUKHONG | Other end meter used for drawal computation; time drift corrective action required
3 | ASSAM | BTPS | AM-28 | 220 kV BTPS_NTPC line 2 | NP-5318-A | Meter data could not be downloaded | 2025-04-07 | Till end of the week | BTPS | Meter replacement in consultation with CTU
2. समय बहाव रिपोर्ट/ Time Drift Report
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation |  | फीडर का नाम / Name of the feeder | मीटर संख्या /Meter Number | वर्ग / Category | टिप्पणी / Remarks
1 | ARUNACHAL PRADESH | DEOMALI |  | 220 kV DEOMALI- KATHALGURI FDR | NP-9659-A | Standby Meter | Weekly Drift correction required
2 | NEEPCO | KHANDONG |  | Khnd. Stage_II | NE-0091-A | Check Meter | Weekly Drift correction required
2 | NEEPCO | KHANDONG |  | Khleihriat-II | NE-0066-A | Check Meter | Weekly Drift correction required
3 | NEEPCO | KHANDONG |  | 3 Mva X’er | NE-0172-A | Check Meter | Weekly Drift correction required
4 | NEEPCO | KHANDONG |  | Khnd. Stage_II M/c | NE-0140-A | Main Meter | Weekly Drift correction required
4 | KMTL | NEW KOHIMA |  | New Kohima-Imphal Line-2 (Bay-406) | NP-9971-A | Standby Meter | Weekly Drift correction required
5 | ASSAM | UMRANGSHO |  | 132 Kv UMRANGSOO END OF HAFLONG FDR | NE-0019-A | Main Meter | Weekly Drift correction required
6 | ASSAM | UMRANGSHO |  | Umrangso- Khliehriat (Khandong) | NP-5290-A | Main Meter | Weekly Drift correction required
11 | ASSAM | PAVOI |  | 132 Kv PAVOI END OF BNC FDR II | NP-8801-A | Main Meter | Weekly Drift correction required
12 | MANIPUR | KARONG |  | 132kV KARONG END OF KOHIMA | NP-9667-A | Main Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | Jiribam- I | NP-9065-A | Check Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | Check meter Imphal-I | NP-9508A | Check Meter | Weekly Drift correction required
15 | NHPC | LOKTAK |  | Check meter Jiribam-II | NP-9511A | Check Meter | Weekly Drift correction required
10 | POWERGRID | MISA |  | ICT#1 400 KV SIDE | NP 5300 A | Standby Meter | Weekly Drift correction required
7 | POWERGRID | HAFLONG |  | BAY NO 102 HAFLONG-UMRANGSHO | NP-8502-A | Standby Meter | Weekly Drift correction required
7 | POWERGRID | MOKOKCHUNG |  | 220/132 kV ICT-1 (LV Side) | NP-9923-A | Standby Meter | Weekly Drift correction required
16 | POWERGRID | NIRJULI |  | ICT-II HV | NP-9662 A | Standby Meter | Weekly Drift correction required
17 | POWERGRID | NIRJULI |  | 132kV Nirjuli-Lekhi(Nirjuli End) | NP-9664 A | Standby Meter | Weekly Drift correction required
18 | POWERGRID | BONGAIGAON |  | 220 KV Line-02 (Bay 03) of Salakati | NP-5780-A | Standby Meter | Weekly Drift correction required
19 | POWERGRID | BONGAIGAON |  | 400/220/33KV ICT (LV Side) Bay 02 | NP-5774-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | DIMAPUR |  | KOHIMA | NP-8472-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BNC |  | LOWER SUBANSIRI-CKT-2 | NE-0150-A | Standby Meter | Weekly Drift correction required
20 | POWERGRID | BNC |  | POLE I | NP-7601-A | Main Meter | Weekly Drift correction required
20 | POWERGRID | BNC |  | 132 Kv BNC- PAVOI Ckt-I (BNC end) | NP-9678-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 220/132 KV ICT-2(HV) | NP-6151-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 400KV BONG#2 | NE-0047-A | Standby Meter | Weekly Drift correction required
21 | POWERGRID | BALIPARA |  | 400KV BONG#3 | NE-0044-A | Standby Meter | Weekly Drift correction required
| STERLITE | NANGALBIBRA_ISTS |  | 221 KV Nangalbibra-Bongaigaon CKT-2 ( Bay 212) | NE-0072-A | Standby Meter | Weekly Drift correction required
22 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 8799 - A | Main Meter | Weekly Drift correction required
23 | NEEPCO | DOYANG |  | 132Kv Doyang-Sanis-Wokha | NP - 9585 - A | Check Meter | Weekly Drift correction required
24 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9066 - A | Main Meter | Weekly Drift correction required
25 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- I | NP - 9584 - A | Check Meter | Weekly Drift correction required
26 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9050 - A | Main Meter | Weekly Drift correction required
27 | NEEPCO | DOYANG |  | 132Kv Doyang-Dimapur- II | NP - 9481 - A | Check Meter | Weekly Drift correction required
28 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9053 - A | Main Meter | Weekly Drift correction required
29 | NEEPCO | DOYANG |  | 132Kv Doyang-Mokokchung | NP - 9516 - A | Check Meter | Weekly Drift correction required
3. टाइम ड्रिफ्ट रिपोर्ट अनुपलब्धता/ Time Drift Report Non Availability
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | MIZORAM | KOLASIB | Time drift report not received
2 | TRIPURA | UDAIPUR | Time drift report not received
3 | TRIPURA | DHARMANAGAR | Time drift report not received
4 | MIZORAM | LUANGMUAL | Time drift report not received
5 | MANIPUR | TIPAIMUKH | Time drift report not received
6 | TRIPURA | AMBASSA | Time drift report not received
7 | NEEPCO | AGBPP | Time drift report not received
8 | NEEPCO | DOYANG | Time drift report not received
9 | NTPC | BGTPP | Time drift report not received
10 | NTPC | PANYOR LOWER | Time drift report not received
11 | ARUNACHAL PRADESH | TENGA | Time drift report not received
12 | MEGHALAYA | UMTRU | Time drift report not received
13 | MEGHALAYA | KOHIMA | Time drift report not received
14 | MEGHALAYA | SANIS | Time drift report not received
15 | POWERGRID | DIMAPUR | Time drift report not received
16 | POWERGRID | SALAKATI | Time drift report not received
4. मीटर डेटा प्राप्त न होना/प्राप्त होने में देरी/ Non receipt/ Delay in receipt of meter data
क्रम संख्या / Sl. N. | उपयोगिता का नाम /Utility Name | स्थान /सबस्टेशन Location /Substation | टिप्पणी / Remarks
1 | TRIPURA | AMBASSA | Not Received. Mailed to concerened
2 | MANIPUR | TIPAIMUKH | Not Received. Mailed to concerened
3 | TRIPURA | UDAIPUR | Not Received. Mailed to concerened
4 | TRIPURA | DHARMANAGAR | Not Received. Mailed to concerened
5 | ASSAM | KAHELIPARA | Mail Received on 17-04-2025
6 | ASSAM | SARUSAJAI | Mail Received on 17-04-2025
7 | ASSAM | MARIANI_AS | Mail Received on 16-04-2025
8 | ASSAM | SAMAGURI | Mail Received on 16-04-2025
9 | POWERGRID | BALIPARA | Mail Received on 16-04-2025
10 | POWERGRID | SALAKATI | Mail Received on 16-04-2025
11 | POWERGRID | SILCHAR | Mail Received on 16-04-2025
12 | POWERGRID | HAFLONG | Mail Received on 16-04-2025
13 | POWERGRID | RANGIA | Mail Received on 16-04-2025
14 | POWERGRID | MARIANI_PG | Mail Received on 16-04-2025
15 | POWERGRID | BONGAIGAON | Mail Received on 16-04-2025
16 | NEEPCO | AGBPS | Mail Received on 16-04-2025
17 | NEEPCO | KHANDONG | Data for NS-2607-A, NS-2640-A and NS-2622-A not received